## Front_page
Field settings table
Applicable indoor units
EKHWET90BAV3
EKHWET(U)120BAV3
Notes
(*1) | EKHWET90+120
(*2) | EKHWETU120

## 4P688157-1D_2024_07
Field settings table |  |  |  |  | Installer setting at variance with default value
Breadcrumb | Field code | Setting name |  | Range, step Default value | Date | Value
Tank
5.2 | [6-0A] | Comfort setpoint | R/W | 30~[6-0E]°C, step: 1°C 50°C
5.3 | [6-0B] | Eco setpoint | R/W | 30~min(50, [6-0E])°C, step: 1°C 45°C
5.4 | [6-0C] | Reheat setpoint | R/W | 30~min(50, [6-0E])°C, step: 1°C 45°C
5.6 | [6-0D] | Heat up mode | R/W | 0: Reheat only 1: Reheat + sched. 2: Scheduled only
└─ | Disinfection
5.7.1 | [2-01] | Activation | R/W | 0: No 1: Yes
5.7.2 | [2-00] | Operation day | R/W | 0: Each day 1: Monday 2: Tuesday 3: Wednesday 4: Thursday 5: Friday 6: Saturday 7: Sunday
5.7.3 | [2-02] | Start time | R/W | 0~23 hour, step: 1 hour 1
5.7.4 | [2-03] | Tank setpoint | R/W | 55-max(55, 6-0E)~75°C, step: 1°C (*1) 55-max(55, 6-0E)~70°C, step: 1°C (*2) 70°C
5.7.5 | [2-04] | Duration | R/W | 5~60 min, step: 5 min 10 min
Tank
5.8 | [6-0E] | Maximum | R/W | 40~75°C, step: 1°C (*1) 40~70°C, step: 1°C (*2) 75°C (*1) 70°C (*2)
5.9 | [6-00] | Hysteresis | R/W | 2~20°C, step: 1°C 6°C
5.A | [6-08] | Hysteresis | R/W | 2~20°C, step: 1°C 10°C
5.B |  | Setpoint mode | R/W | 0: Fixed 1: Weather dependent
└─ | WD curve
5.C | [0-0B] | Setting temperature water value for high ambient temp. for DHW WD curve. | R/W | 35~[6-0E]°C, step: 1°C 43°C
5.C | [0-0C] | Setting temperature water value for low ambient temp. for DHW WD curve. | R/W | 45~[6-0E]°C, step: 1°C 50°C
5.C | [0-0D] | High ambient temp. for DHW WD curve. | R/W | 10~25°C, step: 1°C 25°C
5.C | [0-0E] | Low ambient temp. for DHW WD curve. | R/W | -40~5°C, step: 1°C -15°C
Tank
5.D | [6-01] | Margin | R/W | 0~10°C, step: 1°C 2°C
5.F | [A-00] | Priority schedule | R/W | 0: DHW 1: Air Conditioning
5.G | [A-01] | Operation mode | R/W | 0: Efficient 1: Quick
5.H | [8-03] | Quick mode timer | R/W | Turbo: 10 min Normal: 20 min Economic: 30 min
User settings
└─ | Quiet
7.4.1 |  | Mode | R/W | 0: OFF 1: Manual 2: Automatic
7.4.3 |  | Level | R/W | 0: Quiet 1: More Quiet 2: Most Quiet
Installer settings
└─ | Configuration wizard
| └─ | System
9.1.3.3 | [E-05] [E-06] [E-07] | Domestic hot water | R/O | Integrated
9.1.3.4 | [4-06] | Emergency | R/W | 0: Manual 1: Automatic
9.1.3.7 | [6-02] | BSH capacity | R/W | 0~10kW, step: 0,2kW 1.2kW
| └─ | Tank
9.1.B.1 | [6-0D] | Heat up mode | R/W | 0: Reheat only 1: Reheat + sched. 2: Scheduled only
9.1.B.2 | [6-0A] | Comfort setpoint | R/W | 30~[6-0E]°C, step: 1°C 50°C
9.1.B.3 | [6-0B] | Eco setpoint | R/W | 30~min(50, [6-0E])°C, step: 1°C 45°C
9.1.B.4 | [6-0C] | Reheat setpoint | R/W | 30~min(50, [6-0E])°C, step: 1°C 45°C
9.1.B.6 | [6-08] | Reheat hysteresis | R/W | 2~20°C, step: 1°C 10°C
└─ | Booster heater
9.4.1 | [6-02] | Capacity | R/W | 0~10kW, step: 0,2kW 1.2kW
9.4.3 | [8-03] | Quick mode timer | R/W | 5~95 min, step: 5 min 20 min
9.4.4 | [4-03] | Operation | R/W | 0: Restricted 1: Allowed 2: Overlap 3: Compressor off
└─ | Emergency
9.5.1 | [4-06] | Emergency | R/W | 0: Manual 1: Automatic
└─ | Power consumption control
9.9.1 | [4-08] | Power consumption control | R/W | 0: No limitation 1: Continuous
9.9.2 | [4-09] | Type | R/W | 0: Current 1: Power
9.9.3 | [5-05] | Limit | R/W | 12~50 A, step: 1 A 12 A
9.9.8 | [5-09] | Limit | R/W | 3~20 kW, step: 0,5 kW 3 kW
9.9.D | [4-01] | Priority heater | R/O | 0: None 1: BSH 2: BUH
└─ | Sensors
9.B.3 | [1-0A] | Averaging time | R/W | 0: No averaging 1: 12 hours 2: 24 hours 3: 48 hours 4: 72 hours
Installer settings
9.E | [3-00] | Auto restart | R/W | 0: No 1: Yes
9.F | [E-08] | Power saving function | R/W | 0: Disabled 1: Enabled
9.G |  | Disable protections | R/W | 0: No 1: Yes
└─ | Overview field settings
9.I | [0-0B] | Setting temperature water value for high ambient temp. for DHW WD curve. | R/W | 35~[6-0E]°C, step: 1°C 43°C
9.I | [0-0C] | Setting temperature water value for low ambient temp. for DHW WD curve. | R/W | 45~[6-0E]°C, step: 1°C 50°C
9.I | [0-0D] | High ambient temp. for DHW WD curve. | R/W | 10~25°C, step: 1°C 25°C
9.I | [0-0E] | Low ambient temp. for DHW WD curve. | R/W | -40~5°C, step: 1°C -15°C
9.I | [1-0A] | What is the averaging time for the outdoor temp? | R/W | 0: No averaging 1: 12 hours 2: 24 hours 3: 48 hours 4: 72 hours
9.I | [2-00] | When should the disinfection function be executed? | R/W | 0: Each day 1: Monday 2: Tuesday 3: Wednesday 4: Thursday 5: Friday 6: Saturday 7: Sunday
9.I | [2-01] | Should the disinfection function be executed? | R/W | 0: No 1: Yes
9.I | [2-02] | When should the disinfection function start? | R/W | 0~23 hour, step: 1 hour 1
9.I | [2-03] | What is the disinfection target temperature? | R/W | 55~max(55, 6-0E), step: 1°C 70°C
9.I | [2-04] | How long must the tank temperature be maintained? | R/W | 5~60 min, step: 5 min 10 min
9.I | [3-00] | Is auto restart of the unit allowed? | R/W | 0: No 1: Yes
9.I | [4-01] | Which electric heater has priority? | R/O | 0: None 1: BSH 2: BUH
9.I | [4-03] | Operation permission of the booster heater. | R/W | 0: Restricted 1: Allowed 2: Overlap 3: Compressor off
9.I | [4-06] | Emergency | R/W | 0: Manual 1: Automatic
9.I | [4-08] | Which power limitation mode is required on the system? | R/W | 0: No limitation 1: Continuous
9.I | [4-09] | Which power limitation type is required? | R/W | 0: Current 1: Power
9.I | [5-05] | What is the requested limit for DI1? | R/W | 12~50 A, step: 1 A 12 A
9.I | [5-09] | What is the requested limit for DI1? | R/W | 3~20 kW, step: 0,5 kW 3 kW
9.I | [6-00] | The temperature difference determining the heat pump ON temperature. | R/W | 2~20°C, step: 1°C 6°C
9.I | [6-01] | The temperature difference determining the heat pump OFF temperature. | R/W | 0~10°C, step: 1°C 2°C
9.I | [6-02] | What is the capacity of the booster heater? | R/W | 0~10kW, step: 0,2kW 1.2kW
9.I | [6-08] | What is the hysteresis to be used in reheat mode? | R/W | 2~20°C, step: 1°C 10°C
9.I | [6-0A] | What is the desired comfort storage temperature? | R/W | 30~[6-0E]°C, step: 1°C 50°C
9.I | [6-0B] | What is the desired eco storage temperature? | R/W | 30~min(50, [6-0E])°C, step: 1°C 45°C
9.I | [6-0C] | What is the desired reheat temperature? | R/W | 30~min(50, [6-0E])°C, step: 1°C 45°C
9.I | [6-0D] | What is the desired DHW production type? | R/W | 0: Reheat only 1: Reheat + sched. 2: Scheduled only
9.I | [6-0E] | What is the maximum DHW temperature setpoint? | R/W | 40~75°C, step: 1°C (*1) 40~70°C, step: 1°C (*2) 75°C (*1) 70°C (*2)
9.I | [7-00] | Domestic hot water booster heater overshoot temperature. | R/W | 0~4°C, step: 1°C 0°C
9.I | [7-01] | Domestic hot water booster heater hysteresis. | R/W | 2~40°C, step: 1°C 2°C
9.I | [8-03] | Booster heater delay timer (or Quick mode timer). | R/W | 5~95 min, step: 5 min 20 min
9.I | [A-00] | Which indoor unit operation is prioritized by outdoor unit? | R/W | 0: DHW 1: Air Conditioning
9.I | [A-01] | Which operation mode is used for domestic hot water production? | R/W | 0: Efficient 1: Quick
9.I | [A-02] | -- |  | 1
9.I | [A-03] | -- |  | 0
9.I | [A-04] | -- |  | 0
9.I | [B-00] | -- |  | 0
9.I | [B-01] | -- |  | 0
9.I | [B-02] | -- |  | 0
9.I | [B-03] | -- |  | 0
9.I | [B-04] | -- |  | 0
9.I | [E-00] | Which type of unit is installed? | R/O | 0~5 4: DHWHP
9.I | [E-01] | Which type of compressor is installed? | R/O | 0
9.I | [E-02] | What is the indoor unit software type? | R/O | 1: Heating only
9.I | [E-04] | Is the power saving function available on the outdoor unit? | R/O | 0: No 1: Yes
9.I | [E-05] | Can the system prepare domestic hot water? | R/W | 0: No 1: Yes
9.I | [E-06] | Is a DHW tank installed in the system? | R/O | 0: No 1: Yes
9.I | [E-07] | What kind of DHW tank is installed? | R/O | 0~8 0: EKHW, small volume 1: Integrated 2: Tank with BSH 3: EKHW, large volume 5: EKHWP 7: Third party tank, small coil 8: Third party tank, large coil
9.I | [E-08] | Power saving function for outdoor unit. | R/W | 0: Disabled 1: Enabled
9.I | [F-0A] | -- |  | 0