{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":51,"n_cols":12,"rows_kept":51,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWS-J-SS"]
[]
[]
[]
[]
["","","","","","EWWS120J-SS","EWWS140J-SS","EWWS150J-SS","EWWS180J-SS","EWWS210J-SS","EWWS240J-SS","EWWS270J-SS"]
["Schalldruckpegel","Kühlung","","Nom.","dBA","79","79","79","79","79","79","79"]
["Betriebsbereich","Wasserseite","Verdampfer","Min.","°C TK","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","°C TK","15","15","15","15","15","15","15"]
["Verdichter","Typ","","","","Monoschraubenverdichter","Monoschraubenverdichter","Monoschraubenverdichter","Monoschraubenverdichter","Monoschraubenverdichter","Monoschraubenverdichter","Monoschraubenverdichter"]
["","Startmethode","","","","Ypsilon-Dreieck","Ypsilon-Dreieck","Ypsilon-Dreieck","Ypsilon-Dreieck","Ypsilon-Dreieck","Ypsilon-Dreieck","Ypsilon-Dreieck"]
["","Anzahl_","","","","1","1","1","1","1","1","1"]
["Gewicht","Betriebsgewicht","","","kg","1,211","1,276","1,378","1,415","1,473","1,663","1,675"]
["","Maßeinheit","","","kg","1,177","1,233","1,334","1,366","1,416","1,600","1,607"]
["EER","","","","","3.85","3.75","3.72","3.78","3.82","3.67","3.66"]
["Kältemittel","Typ","","","","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A"]
["","GWP","","","","630","630","630","630","630","630","630"]
["","Kreisläufe","","Anzahl","","1","1","1","1","1","1","1"]
["","Füllmenge","","","kg","18","35","34","37","37","38","38"]
["Kühlleistung","Nom.","","","kW","115.2","136.3","154.7","180.6","207.3","241","272.2"]
["IPLV","","","","","4.1","4.11","4.09","4.11","4.12","4.64","4.59"]
["Rohrleitungsanschlüsse","Wassereinlass / -auslass Verdampfer (AD)","","","","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm"]
["SEER","","","","","3.36","3.38","3.32","3.4","3.39","3.87","3.82"]
["Leistungsaufnahme","Kühlung","","Nom.","kW","30","36.3","41.7","47.8","54.2","65.7","74.4"]
["Sound power level","Kühlung","","Nom.","dBA","89","89","89","89","89","89","89"]
["Abmessungen","Maßeinheit","","Breite","mm","913","913","913","913","913","913","913"]
["","","","Tiefe","mm","2,684","2,684","2,684","2,684","2,684","2,684","2,684"]
["","","","Höhe","mm","1,020","1,020","1,020","1,020","1,020","1,020","1,020"]
["Leistungsregelung","Mindestleistung","","","%","25","25","25","25","25","25","25"]
["","Verfahren","","","","Stufenlos","Stufenlos","Stufenlos","Stufenlos","Stufenlos","Stufenlos","Stufenlos"]
["Gehäuse","Material","","","","Galvanisiertes und lackiertes Stahlblech","Galvanisiertes und lackiertes Stahlblech","Galvanisiertes und lackiertes Stahlblech","Galvanisiertes und lackiertes Stahlblech","Galvanisiertes und lackiertes Stahlblech","Galvanisiertes und lackiertes Stahlblech","Galvanisiertes und lackiertes Stahlblech"]
["","Farbe","","","","Elfenbeinweiß","Elfenbeinweiß","Elfenbeinweiß","Elfenbeinweiß","Elfenbeinweiß","Elfenbeinweiß","Elfenbeinweiß"]
["Wasserwärmetauscher - Verdampfer","Typ","","","","Plattenwärmetauscher.","Plattenwärmetauscher.","Plattenwärmetauscher.","Plattenwärmetauscher.","Plattenwärmetauscher.","Plattenwärmetauscher.","Plattenwärmetauscher."]
["","Wasserdruckabfall","Kühlung","Nom.","kPa","17.1","16.8","32.8","33.4","31.8","27.9","34.8"]
["","Wasservolumen","","","l","14","18","14","17","20","26","26"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~"]
["","Spannungsbereich","","Max.","%","10","10","10","10","10","10","10"]
["","","","Min.","%","-10","-10","-10","-10","-10","-10","-10"]
["","Frequenz","","","Hz","50","50","50","50","50","50","50"]
["","Spannung","","","V","400","400","400","400","400","400","400"]
["Gerät","Max. Gerätestrom für Kabelgrößen","","","A","89","107","120","136","158","183","207"]
["","Anlaufstrom","","Max.","A","154","154","154","154","154","154","154"]
["","Betriebsstrom","Kühlung","Nom.","A","50","60","70","78","87","105","117"]
["","","","Max.","A","81","96","108","122","141","164","185"]
["Hinweise","","","","","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK"]
["","","","","","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK"]
["","","","","","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(5) - Entsprechend EN 14825","(5) - Entsprechend EN 14825","(5) - Entsprechend EN 14825","(5) - Entsprechend EN 14825","(5) - Entsprechend EN 14825","(5) - Entsprechend EN 14825","(5) - Entsprechend EN 14825"]
["","","","","","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung."]
["","","","","","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung."]