{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":47,"n_cols":12,"rows_kept":47,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYA-DV3P-H-"]
[]
[]
[]
[]
["","","","","","EWYA004D2V3P-H","EWYA006D2V3P-H","EWYA008D2V3P-H","EWYA009DAV3P-H-","EWYA011DAV3P-H-","EWYA014DAV3P-H-","EWYA016DAV3P-H-"]
["Kühlleistung","Nom.","","","kW","4.86 (1), 4.52 (2)","5.83 (1), 5.09 (2)","6.18 (1), 5.44 (2)","9.35 (1), 9.10 (2)","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Leistungsregelung","Verfahren","","","","Variabel (Inverter)","Variabel (Inverter)","Variabel (Inverter)","Variabel (Inverter)","Variabel (Inverter)","Variabel (Inverter)","Variabel (Inverter)"]
["Leistungsaufnahme","Kühlung","","Nom.","kW","0.820 (1), 1.36 (2)","1.08 (1), 1.55 (2)","1.19 (1), 1.73 (2)","2.79 (1), 1.71 (2)","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["EER","","","","","5.91 (1), 3.32 (2)","5.40 (1), 3.28 (2)","5.19 (1), 3.14 (2)","3.35 (1), 5.34 (2)","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["SEER","","","","","","","","5.62 (5)","5.79 (5)","5.71 (5)","5.59 (5)"]
["Abmessungen","Maßeinheit","","Tiefe","mm","362","362","362","460","460","460","460"]
["","","","Höhe","mm","770","770","770","870","870","870","870"]
["","","","Breite","mm","1250","1250","1250","1380","1380","1380","1380"]
["Gewicht","Maßeinheit","","","kg","88","88","88","147","147","147","147"]
["Gehäuse","Farbe","","","","Elfenbeinweiß","Elfenbeinweiß","Elfenbeinweiß","Elfenbeinweiß","Elfenbeinweiß","Elfenbeinweiß","Elfenbeinweiß"]
["","Material","","","","Verzinktes Stahlblech","Verzinktes Stahlblech","Verzinktes Stahlblech","Polyesterlackiertes galvanisiertes Stahlblech","Polyesterlackiertes galvanisiertes Stahlblech","Polyesterlackiertes galvanisiertes Stahlblech","Polyesterlackiertes galvanisiertes Stahlblech"]
["Luftwärmetauscher","Typ","","","","","","","Hochleistungs-Rippenrohrtyp mit integriertem Unterkühler","Hochleistungs-Rippenrohrtyp mit integriertem Unterkühler","Hochleistungs-Rippenrohrtyp mit integriertem Unterkühler","Hochleistungs-Rippenrohrtyp mit integriertem Unterkühler"]
["Ventilator","Anzahl","","","","1","1","1","1","1","1","1"]
["","Typ","","","","Flügelventilator","Flügelventilator","Flügelventilator","Flügelventilator","Flügelventilator","Flügelventilator","Flügelventilator"]
["Ventilatormotor","Antrieb","","","","","","","Direktantrieb","Direktantrieb","Direktantrieb","Direktantrieb"]
["Verdichter","Anzahl","","","","1","1","1","1","1","1","1"]
["Verdichter","Typ","","","","Vollhermetischer Swing-Verdichter","Vollhermetischer Swing-Verdichter","Vollhermetischer Swing-Verdichter","Vollhermetischer Swing-Inverter-Verdichter","Vollhermetischer Swing-Inverter-Verdichter","Vollhermetischer Swing-Inverter-Verdichter","Vollhermetischer Swing-Inverter-Verdichter"]
["Verdichter","Startmethode","","","","","","","Invertergeregelt","Invertergeregelt","Invertergeregelt","Invertergeregelt"]
["Betriebsbereich","Luftseite","Kühlung","Min.","°CTK","10 (3)","10 (3)","10 (3)","10","10","10","10"]
["","","","Max.","°CTK","43","43","43","43","43","43","43"]
["","Wasserseite","Verdampfer","Betriebsbereich-=-Wasserseite-=-Verdampfer-=-Min.-=-°C&nbsp;TK","°CTK","5 (3)","5 (3)","5 (3)","5","5","5","5"]
["","","","Betriebsbereich-=-Wasserseite-=-Verdampfer-=-Max.-=-°C&nbsp;TK","°CTK","22","22","22","22","22","22","22"]
["Schallleistungspegel","Kühlung","","Nom.","dBA","61","62","62","65.5","67.0","69.0","69.0"]
["Schalldruckpegel","Kühlung","","Schalldruckpegel-=-Kühlung-=-Nom.-=-dBA","dBA","48","49","50","44.0","47.7","50.8","51.0"]
["Kältemittel","Typ","","","","R-32","R-32","R-32","R-32","R-32","R-32","R-32"]
["","GWP","","","","675","675","675","675.0","675.0","675.0","675.0"]
["","Füllmenge","","","kg","1.35","1.35","1.35"]
["","Kreisläufe","","Anzahl","","","","","1","1","1","1"]
["Stromversorgung","Phase","","","","1~","1~","1~","1~","1~","1~","1~"]
["","Frequenz","","","Hz","50","50","50","50","50","50","50"]
["Spannungsversorgung","Spannung","","","V","230 +/-10%","230 +/-10%","230 +/-10%","230","230","230","230"]
["","Spannungsbereich","","Min.","%","","","","-10","-10","-10","-10"]
["","","","Max.","%","","","","10","10","10","10"]
["Gerät","Betriebsstrom","","Max.","A","","","","30.8","30.8","30.8","30.8"]
["Hinweise","","","","","(1) - Bedingung 1: Kühlen: Ta 35°C - LWE 18°C (DT = 5°C); Heizen: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(1) - Bedingung 1: Kühlen: Ta 35°C - LWE 18°C (DT = 5°C); Heizen: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(1) - Bedingung 1: Kühlen: Ta 35°C - LWE 18°C (DT = 5°C); Heizen: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK"]
["","","","","","(2) - Bedingung 2: Kühlen: Ta 35°C - LWE 7℃ (DT = 5°C); Heizen: Ta TK/FK 7°C/6°C - LWC 45℃ (DT = 5°C)","(2) - Bedingung 2: Kühlen: Ta 35°C - LWE 7℃ (DT = 5°C); Heizen: Ta TK/FK 7°C/6°C - LWC 45℃ (DT = 5°C)","(2) - Bedingung 2: Kühlen: Ta 35°C - LWE 7℃ (DT = 5°C); Heizen: Ta TK/FK 7°C/6°C - LWC 45℃ (DT = 5°C)","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK"]
["","","","","","(3) - Weitere Informationen in der Betriebsbereichszeichnung.","(3) - Weitere Informationen in der Betriebsbereichszeichnung.","(3) - Weitere Informationen in der Betriebsbereichszeichnung.","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","","","","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","","","","(5) - Entsprechend EN 14825","(5) - Entsprechend EN 14825","(5) - Entsprechend EN 14825","(5) - Entsprechend EN 14825"]
["","","","","","","","","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung."]
["","","","","","","","","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung."]