{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":53,"n_cols":7,"rows_kept":53,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYK-QZ"]
[]
[]
[]
[]
["","","","","","EWYK100QZXSA2","EWYK135QZXSA2"]
["Kühlleistung","Nom.","","","kW","91.3","128.30"]
["Leistungsregelung","Verfahren","","","","Invertergeregelt","Invertergeregelt"]
["","Mindestleistung","","","%","15","11"]
["Leistungsaufnahme","Kühlung","","Nom.","kW","30.43","48.42"]
["EER","","","","","3.00","2.65"]
["IPLV","","","","","6.24","5.94"]
["SEER","","","","","5.06","4.81"]
["Abmessungen","Maßeinheit","","Tiefe","mm","1207","1207"]
["","","","Höhe","mm","2382","2382"]
["","","","Breite","mm","2653","2653"]
["Gewicht","Betriebsgewicht","","","kg","1195","1272"]
["","Maßeinheit","","","kg","1166","1239"]
["Gehäuse","Farbe","","","","Elfenbeinweiß","Elfenbeinweiß"]
["","Material","","","","Galvanisiertes und lackiertes Stahlblech","Galvanisiertes und lackiertes Stahlblech"]
["Luftwärmetauscher","Typ","","","","Al-Lamellen und Cu-Rohre","Al-Lamellen und Cu-Rohre"]
["Ventilator","Anzahl","","","","2","2"]
["","Typ","","","","Axial","Axial"]
["","Luftvolumenstrom","Kühlung","Nom.","l/s","12600","14160"]
["Ventilatormotor","Antrieb","","","","Bürstenlos","Bürstenlos"]
["Verdichter","Anzahl","","","","2","2"]
["","Typ","","","","Scroll","Scroll"]
["Betriebsbereich","Luftseite","Kühlung","Min.","°C TK","-20","-20"]
["","","","Max.","°C TK","46","46"]
["","Wasserseite","Verdampfer","Betriebsbereich-=-Wasserseite-=-Verdampfer-=-Min.-=-°C TK","°C TK","20","20"]
["","","","Betriebsbereich-=-Wasserseite-=-Verdampfer-=-Max.-=-°C TK","°C TK","75","75"]
["Schallleistungspegel","Kühlung","","Nom.","dB(A)","86.3","90.9"]
["Schalldruckpegel","Kühlung","","Nom.","dB(A)","68.1","72.7"]
["Kältemittel","Typ","","","","R-290","R-290"]
["","GWP","","","","0.02","0.02"]
["","Füllmenge","","","kg","6.3","6.6"]
["","Kreisläufe","","Anzahl","","2","2"]
["Rohrleitungsanschlüsse","Wassereinlass / -auslass Verdampfer (AD)","","","","3\"","3\""]
["Stromversorgung","Phase","","","","3","3"]
["","Frequenz","","","Hz","50","50"]
["Spannungsversorgung","Spannung","","","V","400","400"]
["","Spannungsbereich","","Min.","%","-10","-10"]
["","","","Max.","%","10","10"]
["Gerät","Anlaufstrom","","Max.","A","0","0"]
["","Betriebsstrom","Kühlung","Nom.","A","52.1","82.8"]
["","","","Max.","A","122.0","142.0"]
["","Max. Gerätestrom für Kabelgrößen","","","A","134.0","156.0"]
["Hinweise","","","","","(1) - Kühlen: Wassertemp. Verdampfereintritt 12°C, Wassertemp. Verdampferaustritt 7°C, Umgebungstemp. 35°C","(1) - Kühlen: Wassertemp. Verdampfereintritt 12°C, Wassertemp. Verdampferaustritt 7°C, Umgebungstemp. 35°C"]
["","","","","","(2) - Bedingung: Außentemperatur 7°C TK, 6°CFK; LWC 35°C (DT = 5°C)","(2) - Bedingung: Außentemperatur 7°C TK, 6°CFK; LWC 35°C (DT = 5°C)"]
["","","","","","(3) - Entsprechend EN14825","(3) - Entsprechend EN14825"]
["","","","","","(4) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(4) - Von der Betriebsart abhängig, siehe Installationsanleitung."]
["","","","","","(5) - Weitere Informationen in der Betriebsbereichszeichnung.","(5) - Weitere Informationen in der Betriebsbereichszeichnung."]
["","","","","","(6) - Performance data calculated as Chiller Configurator - 2.0.0","(6) - Performance data calculated as Chiller Configurator - 2.0.0"]