{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":59,"n_cols":12,"rows_kept":59,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXS-K"]
[]
[]
[]
[]
["","","","","","RXS20K3V1B","RXS20K2V1B","RXS25K3V1B","RXS25K2V1B","RXS35K2V1B","RXS42K2V1B","RXS50K2V1B"]
["Schalldruckpegel","Heizen","","Hoch","dBA","47","","47","","48","48","48"]
["","Kühlung","","Hoch","dBA","46","","46","","48","48","48"]
["Standardzubehör","Verbindung (Ableitung)","","","","1","","1"]
["","Installationsanleitung","","","","1","","1","","1","1","1"]
["Kältemittel","Charge","","","TCO2-Äquivalent","2.1","","2.1","","2.5","2.7","3.5"]
["","GWP","","","","2,087.5","","2,087.5","","2,087.5","2,087.5","2,087.5"]
["","Füllmenge","","","kg","1.0","","1.0","","1.2","1.3","1.7"]
["","Typ","","","","R-410A","","R-410A","","R-410A","R-410A","R-410A"]
["Ventilatormotor","Drehzahl","Kühlung","Sehr niedrig","U/min","780","","780","","780","790","670"]
["","","Heizen","Sehr niedrig","U/min","740","","740","","740","780","670"]
["Rohrleitungsanschlüsse","Niveauunterschied","IG - AG","Max.","M","15","","15","","15","15","20"]
["","Zusätzliche Kältemittelfüllmenge","","","kg/m","0,02 (für Rohrleitungslängen über 10 m)","","0,02 (für Rohrleitungslängen über 10 m)","","0,02 (für Rohrleitungslängen über 10 m)","0,02 (für Rohrleitungslängen über 10 m)","0,02 (für Rohrleitungslängen über 10 m)"]
["Verdichter","Typ","","","","Vollhermetischer Schwingverdichter","","Vollhermetischer Schwingverdichter","","Vollhermetischer Schwingverdichter","Vollhermetischer Schwingverdichter","Vollhermetischer Schwingverdichter"]
["Abmessungen","Maßeinheit","","Breite","mm","765","","765","","765","765","825"]
["","","","Tiefe","mm","285","","285","","285","285","300"]
["","","","Höhe","mm","550","","550","","550","550","735"]
["Gewicht","Maßeinheit","","","kg","34","","34","","34","39","47"]
["Ventilator","Luftstromvolumen","Heizen","Sehr niedrig","cfm","","","","","904","960","1,522"]
["","","Kühlung","Sehr niedrig","cfm","","","","","1,063","1,080","1,727"]
["Spannungsversorgung","Phase","","","","1~","","1~","","1~","1~","1~"]
["","Frequenz","","","Hz","50","","50","","50","50","50"]
["","Spannung","","","V","220-240","","220-240","","220-240","220-240","220-240"]
["Hinweise","","","","","(1) - 220 V","(1) - 220 V","(1) - 220 V","(1) - 220 V","(1) - 220 V","(1) - 220 V","(1) - 220 V"]
["","","","","","(2) - 230 V","(2) - 230 V","(2) - 230 V","(2) - 230 V","(2) - 230 V","(2) - 230 V","(2) - 230 V"]
["","","","","","(3) - 240 V","(3) - 240 V","(3) - 240 V","(3) - 240 V","(3) - 240 V","(3) - 240 V","(3) - 240 V"]
["","","","","","(4) - SL: Die flüsterleise Ventilatorstufe der Luftmengeneinstellung.","","(4) - SL: Die flüsterleise Ventilatorstufe der Luftmengeneinstellung.","","(4) - Enthält fluorierte Treibhausgase","(4) - Enthält fluorierte Treibhausgase","(4) - Enthält fluorierte Treibhausgase"]
["","","","","","(5) - Enthält fluorierte Treibhausgase","","(5) - Enthält fluorierte Treibhausgase"]
["Abmessungen","Maßeinheit","","Höhe","mm","","550","","550"]
["","","","Breite","mm","","765","","765"]
["","","","Tiefe","mm","","285","","285"]
["Gewicht","Maßeinheit","","","kg","","34","","34"]
["Ventilatormotor","Drehzahl","Kühlung","Sehr niedrig","U/min","","780","","780"]
["","","Heizen","Sehr niedrig","U/min","","740","","740"]
["Verdichter","Typ","","","","","Vollhermetischer Swing-Verdichter","","Vollhermetischer Swing-Verdichter"]
["Betriebsbereich","Kühlung","Umgebung","Min.","°C TK","","-10","","-10"]
["","","","Max.","°C TK","","46","","46"]
["","Heizen","Umgebung","Min.","°C FK","","-15","","-15"]
["","","","Max.","°C FK","","18","","18"]
["Schalldruckpegel","Kühlung","","Hoch","dBA","","46","","46"]
["","Heizen","","Hoch","dBA","","47","","47"]
["Kältemittel","Typ","","","","","R-410A","","R-410A"]
["","Füllmenge","","","kg","","1.0","","1.0"]
["","Füllmenge","","","tCO2Eq","","2.1","","2.1"]
["","GWP","","","","","2087.5","","2087.5"]
["Rohrleitungsanschlüsse","Leitungslänge","Max.","AG – IG","M","","20","","20"]
["","Zusätzliche Kältemittelfüllmenge","","","kg/m","","0,02 (für Rohrleitungslängen über 10 m)","","0,02 (für Rohrleitungslängen über 10 m)"]
["","Niveauunterschied","IG - AG","Max.","M","","15","","15"]
["Standardzubehör","Installation manual","","","","","1","","1"]
["","Joint (drain)","","","","","1","","1"]
["Stromversorgung","Phase","","","","","1~","","1~"]
["","Frequenz","","","Hz","","50","","50"]
["Spannungsversorgung","Spannung","","","V","","220-240","","220-240"]
["Standardzubehör","Ablassstopfen","","","","","","","","1","1","1"]