{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":41,"n_cols":13,"rows_kept":41,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZAG-NY1"]
[]
[]
[]
[]
["","","","","","RZAG71N2Y1B","RZAG71N7Y1B","RZAG100N7Y1B","RZAG100N2Y1B","RZAG125N7Y1B","RZAG125N2Y1B","RZAG140N2Y1B","RZAG140N7Y1B"]
["Abmessungen","Maßeinheit","","Höhe","mm","870","870","870","870","870","870","870","870"]
["","","","Breite","mm","1100","1100","1100","1100","1100","1100","1100","1100"]
["","","","Tiefe","mm","460","460","460","460","460","460","460","460"]
["Gewicht","Maßeinheit","","","kg","81","81","85","85","94","94","94","94"]
["Verdichter","Typ","","","","Vollhermetischer Swing-Verdichter","Vollhermetischer Swing-Verdichter","Vollhermetischer Swing-Verdichter","Vollhermetischer Swing-Verdichter","Vollhermetischer Swing-Verdichter","Vollhermetischer Swing-Verdichter","Vollhermetischer Swing-Verdichter","Vollhermetischer Swing-Verdichter"]
["Betriebsbereich","Kühlung","Umgebung","Min.","°C TK","-20","-20","-20","-20","-20","-20","-20","-20"]
["","","","Max.","°C TK","52","52","52","52","52","52","52","52"]
["","Heizen","Umgebung","Betriebsbereich-=-Heizen-=-Umgebung-=-Min.-=-°C FK","°C FK","-20","-20","-20","-20","-20","-20","-20","-20"]
["","","","Betriebsbereich-=-Heizen-=-Umgebung-=-Max.-=-°C FK","°C FK","18","18","18","18","18","18","18","18"]
["Schallleistungspegel","Kühlung","","","dB(A)","64","64","66","66","69","69","70","70"]
["","Heizen","","","dB(A)","","","","","68 (1)","68 (1)","71 (1)","71 (1)"]
["Schalldruckpegel","Kühlung","","Nom.","dB(A)","46","46","47","47","49","49","50","50"]
["","Heizen","","Nom.","dB(A)","48","48","50","50","52","52","52","52"]
["Kältemittel","Typ","","","","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32"]
["","Füllmenge","","","kg","3.20","3.2","3.2","3.20","3.7","3.70","3.70","3.7"]
["","GWP","","","","675","675","675","675","675","675","675","675"]
["","Kältemittel-=-Füllmenge-=-tCO2-Äq.","","","tCO2-Äq.","2.16","2.16","2.16","2.16","2.5","2.50","2.50","2.5"]
["Rohrleitungsanschlüsse","Flüssigkeit","","AD","mm","10","10","10","10","10","10","10","10"]
["","Gas","","AD","mm","15.9","15.9","15.9","15.9","15.9","15.9","15.9","15.9"]
["","Leitungslänge","Max.","AG – IG","m","55","55","85","85","85","85","85","85"]
["","","System","Äquivalent","m","75","75","100","100","100","100","100","100"]
["","","","Unbefüllt","m","40","40","40","40","40","40","40","40"]
["","Zusätzliche Kältemittelfüllmenge","","","kg/m","Siehe Installationsanleitung","Siehe Installationsanleitung","Siehe Installationsanleitung","Siehe Installationsanleitung","Siehe Installationsanleitung","Siehe Installationsanleitung","Siehe Installationsanleitung","Siehe Installationsanleitung"]
["","Niveauunterschied","IG - AG","Max.","m","30","30","30","30","30","30","30","30"]
["","","IG - IG","Max.","m","0.5","0.5","0.5","0.5","0.5","0.5","0.5","0.5"]
["Standardzubehör","Installationsanleitung","","","","1","1","1","1","1","1","1","1"]
["","Kältemitteletikett für F-Gas-Bestimmungen","","","","1","1","1","1","1","1","1","1"]
["","Allgemeine Schutzmaßnahmen","","","","1","1","1","1","1","1","1","1"]
["","F-Gase-Aufkleber abziehen","","","","1","1","1","1","1","1","1","1"]
["","Kabelbinder","","","","2","2","2","2","2","2","2","2"]
["Stromversorgung","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequenz","","","Hz","50","50","50","50","50","50","50","50"]
["Spannungsversorgung","Spannung","","","V","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415"]
["Stromstärke – 50 Hz","Stromstärke – 50 Hz-=-Max. Amperezahl für Sicherung (MFA)-=-A","","","A","16","16","16","16","16","16","16","16"]
["Hinweise","","","","","(1) - Gemäß ENER Lot 21","(1) - Gemäß ENER Lot 21","(1) - Gemäß ENER Lot 21","(1) - Gemäß ENER Lot 21","(1) - Gemäß ENER Lot 21","(1) - Gemäß ENER Lot 21","(1) - Gemäß ENER Lot 21","(1) - Gemäß ENER Lot 21"]