{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":34,"n_cols":9,"rows_kept":34,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZQG-LY1L"]
[]
[]
[]
[]
["","","","","","RZQG71L8Y1L","RZQG100L8Y1L","RZQG125L8Y1L","RZQG140L7Y1L"]
["Schalldruckpegel","Heizen","","Nom.","dBA","50","52","53","53"]
["","Kühlung","","Nom.","dBA","48","50","51","52"]
["Standardzubehör","Kabelbinder","","","","2","2","2","2"]
["","Installationsanleitung","","","","1","1","1","1"]
["Kältemittel","Charge","","","TCO2-Äquivalent","6.10","8.40","8.40","8.40"]
["","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Füllmenge","","","kg","2.9","4.0","4.0","4.0"]
["","Typ","","","","R-410A","R-410A","R-410A","R-410A"]
["Rohrleitungsanschlüsse","Flüssigkeit","","AD","mm","9.52","9.52","9.52","9.52"]
["","Leitungslänge","Max.","AG – IG","M","50","75","75","75"]
["","","System","Unbefüllt","M","30","30","30","30"]
["","","","Äquivalent","M","70","90","90","90"]
["","Gas","","AD","mm","15.9","15.9","15.9","15.9"]
["","Niveauunterschied","IG - IG","Max.","M","0.5","0.5","0.5","0.5"]
["","","IG - AG","Max.","M","30.0","30.0","30.0","30.0"]
["","Zusätzliche Kältemittelfüllmenge","","","kg/m","Siehe Installationsanleitung","Siehe Installationsanleitung","Siehe Installationsanleitung","Siehe Installationsanleitung"]
["Sound power level","Kühlung","","","dBA","64","66","67","69"]
["Verdichter","Typ","","","","Vollhermetischer Schwingverdichter","Vollhermetischer Schwingverdichter","Vollhermetischer Schwingverdichter","Vollhermetischer Schwingverdichter"]
["Abmessungen","Maßeinheit","","Breite","mm","940","940","940","940"]
["","","","Tiefe","mm","320","320","320","320"]
["","","","Höhe","mm","990","1,430","1,430","1,430"]
["Gewicht","Maßeinheit","","","kg","80","101","101","101"]
["Power supply","Phase","","","","3N~","3N~","3N~","3N~"]
["","Frequenz","","","Hz","50","50","50","50"]
["","Spannung","","","V","380-415","380-415","380-415","380-415"]
["Hinweise","","","","","(1) - 3 mit Wiederbefüllung","(1) - 3 mit Wiederbefüllung","(1) - 3 mit Wiederbefüllung","(1) - 3 mit Wiederbefüllung"]
["","","","","","(2) - Siehe separate Zeichnungen für die elektrischen Daten","(2) - Siehe separate Zeichnungen für die elektrischen Daten","(2) - Siehe separate Zeichnungen für die elektrischen Daten","(2) - Siehe separate Zeichnungen für die elektrischen Daten"]
["","","","","","(3) - PED: Anlage = Kategorie I: ausgenommen vom PED-Geltungsbereich aufgrund Artikel 1, Punkt 3.6 von 97/23/EG","(3) - PED: Anlage = Kategorie I: ausgenommen vom PED-Geltungsbereich aufgrund Artikel 1, Punkt 3.6 von 97/23/EG","(3) - PED: Anlage = Kategorie I: ausgenommen vom PED-Geltungsbereich aufgrund Artikel 1, Punkt 3.6 von 97/23/EG","(3) - PED: Anlage = Kategorie I: ausgenommen vom PED-Geltungsbereich aufgrund Artikel 1, Punkt 3.6 von 97/23/EG"]