{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":60,"n_cols":9,"rows_kept":60,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYA-DW1P-H-"]
[]
[]
[]
[]
["","","","","","EWYA009DAW1P-H-","EWYA011DAW1P-H-","EWYA014DAW1P-H-","EWYA016DAW1P-H-"]
["Niveau de pression sonore","Rafraîchissement","","Nom.","dBA","44.0","47.7","50.8","51.0"]
["Composants hydrauliques","Vase d'expansion","","Volume","l","8","8","8","8"]
["Plage de fonctionnement","Côté air","Rafraîchissement","Min.","°CBS","10","10","10","10"]
["","","","Max.","°CBS","43","43","43","43"]
["","","Chauffage","Max.","°CBS","25","25","25","25"]
["","","","Min.","°CBS","-25","-25","-25","-25"]
["","Côté eau","Chauffage","Min.","°CBS","9 (7)","9 (7)","9 (7)","9 (7)"]
["","","","Max.","°CBS","60 (7)","60 (7)","60 (7)","60 (7)"]
["","","Rafraîchissement","Max.","°CBS","22","22","22","22"]
["","","","Min.","°CBS","5","5","5","5"]
["Charge de réfrigérant","Par circuit","","","kg","3.80","3.80","3.80","3.80"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","2.6","2.6","2.6","2.6"]
["Compressor","Type","","","","Compresseur swing hermétique à Inverter","Compresseur swing hermétique à Inverter","Compresseur swing hermétique à Inverter","Compresseur swing hermétique à Inverter"]
["","Starting method","","","","Commandé par Inverter","Commandé par Inverter","Commandé par Inverter","Commandé par Inverter"]
["","Quantité_","","","","1","1","1","1"]
["Échangeur de chaleur air","Type","","","","Type de tube et d'ailette à haut rendement avec sous-refroidisseur intégral","Type de tube et d'ailette à haut rendement avec sous-refroidisseur intégral","Type de tube et d'ailette à haut rendement avec sous-refroidisseur intégral","Type de tube et d'ailette à haut rendement avec sous-refroidisseur intégral"]
["Poids","Unité","","","kg","147","147","147","147"]
["EER","","","","","3.35 (1), 5.34 (2)","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["Réfrigérant","PRP","","","","675.0","675.0","675.0","675.0"]
["","Type","","","","R-32","R-32","R-32","R-32"]
["","Circuits","","Quantité","","1","1","1","1"]
["","Commande","","","","Détendeur électronique","Détendeur électronique","Détendeur électronique","Détendeur électronique"]
["Moteur de ventil.","Vitesse","Rafraîchissement","Nom.","tr/min","500","550","650","650"]
["","","Chauffage","Nom.","tr/min","400","450","550","650"]
["Puissance frigorifique","Nom.","","","kW","9.35 (1), 9.10 (2)","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Échangeur de chaleur - eau","Volume d'eau","","","l","2","2","2","2"]
["","Volume min. d'eau dans le système","","","l","50 (6)","50 (6)","50 (6)","50 (6)"]
["","Type","","","","Échangeur de chaleur à plaques","Échangeur de chaleur à plaques","Échangeur de chaleur à plaques","Échangeur de chaleur à plaques"]
["Puissance absorbée","Rafraîchissement","","Nom.","kW","2.79 (1), 1.71 (2)","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["","Chauffage","","Nom.","kW","1.91 (3), 2.43 (4)","2.18 (3), 2.68 (4)","2.46 (3), 3.42 (4)","3.53 (3), 4.56 (4)"]
["Sound power level","Rafraîchissement","","Nom.","dBA","65.5","67.0","69.0","69.0"]
["COP","","","","","4.91 (3), 3.71 (4)","4.83 (3), 3.66 (4)","4.87 (3), 3.64 (4)","4.53 (3), 3.51 (4)"]
["Dimensions","Unité","","Largeur","mm","1,380","1,380","1,380","1,380"]
["","","","Profondeur","mm","460","460","460","460"]
["","","","Hauteur","mm","870","870","870","870"]
["Commande de puissance","Méthode","","","","Variable (inverter)","Variable (inverter)","Variable (inverter)","Variable (inverter)"]
["Chauffage des locaux","Sortie d'eau sous climat tempéré 55 °C","Général","Seasonal space heating eff. class","","A++","A++","A++","A++"]
["","","","ηs (effic. saisonnière du chauffage d'ambiance)","%","135","132","134","132"]
["","","","SCOP","","3.44","3.37","3.42","3.37"]
["Ventilateur","Débit d'air","Chauffage","Nom.","m³/min","48.0","55.8","70.4","85.0"]
["","","Rafraîchissement","Nom.","m³/min","63","70","85","85"]
["Puissance calorifique","Nom.","","","kW","9.37 (3), 9.00 (4)","10.6 (3), 9.82 (4)","12.0 (3), 12.5 (4)","16.0 (3), 16.0 (4)"]
["Compressor","Starting method","","","","Commande","Commande","Commande","Commande"]
["Power supply","Phase","","","","3~","3~","3~","3~"]
["","Fréquence","","","Hz","50","50","50","50"]
["","Nom","","","","W1","W1","W1","W1"]
["","Tension","","","V","400","400","400","400"]
["Remarques","","","","","(1) - Rafraîchissement : Entrée d'eau 12℃ ; Sortie d'eau 7℃ ; Conditions extérieures : 35 °CBS","(1) - Rafraîchissement : Entrée d'eau 12℃ ; Sortie d'eau 7℃ ; Conditions extérieures : 35 °CBS","(1) - Rafraîchissement : Entrée d'eau 12℃ ; Sortie d'eau 7℃ ; Conditions extérieures : 35 °CBS","(1) - Rafraîchissement : Entrée d'eau 12℃ ; Sortie d'eau 7℃ ; Conditions extérieures : 35 °CBS"]
["","","","","","(2) - Rafraîchissement : Entrée d'eau 23℃ ; Sortie d'eau 18℃ ; Conditions extérieures : 35 °CBS","(2) - Rafraîchissement : Entrée d'eau 23℃ ; Sortie d'eau 18℃ ; Conditions extérieures : 35 °CBS","(2) - Rafraîchissement : Entrée d'eau 23℃ ; Sortie d'eau 18℃ ; Conditions extérieures : 35 °CBS","(2) - Rafraîchissement : Entrée d'eau 23℃ ; Sortie d'eau 18℃ ; Conditions extérieures : 35 °CBS"]
["","","","","","(3) - Condition : Ta DS/BH 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(3) - Condition : Ta DS/BH 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(3) - Condition : Ta DS/BH 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(3) - Condition : Ta DS/BH 7 °C/6 °C - LWC 35 °C (DT = 5 °C)"]
["","","","","","(4) - Condition : Ta BS/BH 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Condition : Ta BS/BH 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Condition : Ta BS/BH 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Condition : Ta BS/BH 7 °C/6 °C - LWC 45 °C (Dt=5 °C)"]
["","","","","","(5) - Conformément à la norme EN14825","(5) - Conformément à la norme EN14825","(5) - Conformément à la norme EN14825","(5) - Conformément à la norme EN14825"]
["","","","","","(6) - En fonction du mode de fonctionnement, voir le manuel d’installation.","(6) - En fonction du mode de fonctionnement, voir le manuel d’installation.","(6) - En fonction du mode de fonctionnement, voir le manuel d’installation.","(6) - En fonction du mode de fonctionnement, voir le manuel d’installation."]
["","","","","","(7) - Pour en savoir plus, se reporter au schéma de plage de fonctionnement.","(7) - Pour en savoir plus, se reporter au schéma de plage de fonctionnement.","(7) - Pour en savoir plus, se reporter au schéma de plage de fonctionnement.","(7) - Pour en savoir plus, se reporter au schéma de plage de fonctionnement."]