{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":34,"n_cols":9,"rows_kept":34,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZQG-LY1L"]
[]
[]
[]
[]
["","","","","","RZQG71L8Y1L","RZQG100L8Y1L","RZQG125L8Y1L","RZQG140L7Y1L"]
["Niveau de pression sonore","Chauffage","","Nom.","dBA","50","52","53","53"]
["","Rafraîchissement","","Nom.","dBA","48","50","51","52"]
["Accessoires standard","Attaches","","","","2","2","2","2"]
["","Manuel d'installation","","","","1","1","1","1"]
["Réfrigérant","Charge","","","TCO2Eq","6.10","8.40","8.40","8.40"]
["","PRP","","","","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","2.9","4.0","4.0","4.0"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A"]
["Raccords de tuyauterie","Liquide","","DE","mm","9.52","9.52","9.52","9.52"]
["","Longueur de tuyauterie","Max.","UE - UI","m","50","75","75","75"]
["","","Système","Préchargé d'usine jusqu'à","m","30","30","30","30"]
["","","","Équivalente","m","70","90","90","90"]
["","Gaz","","DE","mm","15.9","15.9","15.9","15.9"]
["","Dénivelé","UI - UI","Max.","m","0.5","0.5","0.5","0.5"]
["","","UI - UE","Max.","m","30.0","30.0","30.0","30.0"]
["","Charge de réfrigérant supplémentaire","","","kg/m","Voir le manuel d'installation","Voir le manuel d'installation","Voir le manuel d'installation","Voir le manuel d'installation"]
["Niveau de puissance sonore","Rafraîchissement","","","dBA","64","66","67","69"]
["Compresseur","Type","","","","Compresseur swing hermétique","Compresseur swing hermétique","Compresseur swing hermétique","Compresseur swing hermétique"]
["Dimensions","Unité","","Largeur","mm","940","940","940","940"]
["","","","Profondeur","mm","320","320","320","320"]
["","","","Hauteur","mm","990","1,430","1,430","1,430"]
["Poids","Unité","","","kg","80","101","101","101"]
["Power supply","Phase","","","","3N~","3N~","3N~","3N~"]
["","Fréquence","","","Hz","50","50","50","50"]
["","Tension","","","V","380-415","380-415","380-415","380-415"]
["Remarques","","","","","(1) - 3 avec recharge","(1) - 3 avec recharge","(1) - 3 avec recharge","(1) - 3 avec recharge"]
["","","","","","(2) - Pour les données électriques, se reporter aux schémas séparés.","(2) - Pour les données électriques, se reporter aux schémas séparés.","(2) - Pour les données électriques, se reporter aux schémas séparés.","(2) - Pour les données électriques, se reporter aux schémas séparés."]
["","","","","","(3) - DESP : montage = catégorie l : hors du champ d'application DESP en raison de l'article 1, élément 3.6 de la directive 97/23/CE","(3) - DESP : montage = catégorie l : hors du champ d'application DESP en raison de l'article 1, élément 3.6 de la directive 97/23/CE","(3) - DESP : montage = catégorie l : hors du champ d'application DESP en raison de l'article 1, élément 3.6 de la directive 97/23/CE","(3) - DESP : montage = catégorie l : hors du champ d'application DESP en raison de l'article 1, élément 3.6 de la directive 97/23/CE"]