{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":36,"n_cols":11,"rows_kept":36,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXP-N"]
[]
[]
[]
[]
["","","","","","RXP20N5V1B","RXP25N5V1B","RXP35N5V1B","RXP50N5V1B","RXP60N5V1B","RXP71N5V1B"]
["Dimensioni","Unità","","Altezza","mm","556","556","556","734","734","734"]
["","","","Larghezza","mm","740","740","740","954","954","954"]
["","","","Profondità","mm","343","343","343","401","401","401"]
["Peso","Unità","","","kg","24","24","24","46.0","50.0","50.0"]
["Compressor","Tipo","","","","","","","Compressore ermetico tipo Swing"]
["Campo di funzionamento","Raffrescamento","T. esterna","Min.","°CBS","-10","-10","-10","-10","-10","-10"]
["","","","Max.","°CBS","48","48","48","48","48","48"]
["","Riscaldamento","T. esterna","Min.","°CBU","-15","-15","-15"]
["","","","Max.","°CBU","18","18","18"]
["Livello pressione sonora","Raffrescamento","","Alta","dBA","46","46","48"]
["","","","Nom.","dBA","","","","47","49","52"]
["","Riscaldamento","","Alta","dBA","47","47","48"]
["","","","Nom.","dBA","","","","49","49","52"]
["Refrigerante","Tipo","","","","R-32","R-32","R-32","R-32","R-32","R-32"]
["","Carica","","","kg","0.55","0.55","0.70","0.90","1.15","1.15"]
["","Refrigerante-=-Carica-=-TCO2Eq","","","tCO2Eq","0.37","0.37","0.48","0.61","0.78","0.78"]
["","GWP","","","","675.0","675.0","675.0","675","675","675"]
["Collegamenti tubazioni","Lunghezza tubazioni","Max.","est. - int.","m","20","20","20","30","30","30"]
["","Carica di refrigerante aggiuntivo","","","kg/m","0,02 (per lunghezza delle tubazioni superiore ai 10m)","0,02 (per lunghezza delle tubazioni superiore ai 10m)","0,02 (per lunghezza delle tubazioni superiore ai 10m)","0,02 (per lunghezza delle tubazioni superiore ai 10m)","0,02 (per lunghezza delle tubazioni superiore ai 10m)","0,02 (per lunghezza delle tubazioni superiore ai 10m)"]
["","Dislivello","int. - est.","Max.","m","12","12","12","20","20","20"]
["Accessori standard","Installation manual","","","","1","1","1","1","1","1"]
["","Refrigerant charge label","","","","1","1","1","1","1","1"]
["","Multilingual fluorinated greenhouse gases labels","","","","1","1","1","1","1","1"]
["","Drain cap","","","","","","","3","3","3"]
["","Drain plug","","","","1","1","1","1","1","1"]
["Alimentazione","Fase","","","","1~","1~","1~","1~","1~","1~"]
["","Frequenza","","","Hz","50","50","50","50","50","50"]
["","Tensione","","","V","220-240","220-240","220-240","220-240","220-240","220-240"]
["Compressore","Tipo","","","","Compressore ermetico tipo Swing","Compressore ermetico tipo Swing","Compressore ermetico tipo Swing","","Compressore ermetico tipo Swing","Compressore ermetico tipo Swing"]
["Accessori standard","General safety precautions","","","","1","1","1"]