{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":40,"n_cols":6,"rows_kept":40,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXS-F8"]
[]
[]
[]
[]
["","","","","","RXS71FAV1B8"]
["Ventilatore","Portata d'aria","Raffrescamento","Bassissimo","m³;/min","46.0"]
["","","Riscaldamento","Bassissimo","m³;/min","46.0"]
["","","","Bassissimo","cfm","1624"]
["","","Riscaldamento","Bassissimo","cfm","1624"]
["Dimensioni","Unità","","Altezza","mm","770"]
["","","","Larghezza","mm","900"]
["","","","Profondità","mm","320"]
["Peso","Unità","","","kg","71"]
["Motore del ventilatore","Velocità","Raffrescamento","Bassissimo","giri/min","730"]
["","","Riscaldamento","Bassissimo","giri/min","730"]
["Compressore","Tipo","","","","Compressore ermetico tipo Swing"]
["Campo di funzionamento","Raffrescamento","T. esterna","Min.","°CBS","-10"]
["","","","Max.","°CBS","46"]
["","Riscaldamento","T. esterna","Min.","°CBU","-15"]
["","","","Max.","°CBU","18"]
["Livello pressione sonora","Raffrescamento","","Alta","dBA","52"]
["","Riscaldamento","","Alta","dBA","52"]
["Refrigerante","Tipo","","","","R-410A"]
["","Carica","","","kg","2.3"]
["","Refrigerante-=-Carica-=-TCO2Eq","","","tCO2Eq","4.8"]
["","GWP","","","","2087.5"]
["Collegamenti tubazioni","Lunghezza tubazioni","Max.","est. - int.","m","30"]
["","Carica di refrigerante aggiuntivo","","","kg/m","0,02 (per lunghezza delle tubazioni superiore ai 10m)"]
["","Dislivello","int. - est.","Max.","m","20"]
["Accessori standard","Installation manual","","","","1"]
["","Refrigerant charge label","","","","1"]
["","Multilingual fluorinated greenhouse gases labels","","","","1"]
["","Drain socket assy","","","","1"]
["Alimentazione","Fase","","","","1~"]
["","Frequenza","","","Hz","50"]
["","Tensione","","","V","220-240"]
["Note","","","","","(1) - 220V"]
["","","","","","(2) - 230V"]
["","","","","","(3) - 240V"]